## Sheet1
COPPER SILVER IONIZATION SCHEDULE - DOMESTIC HOT WATER LEGIONELLA GROWTH PREVENTION COMPLIANCE
FACILITY ZONE PARAMETERS : DHW | [5 empty] | CSI CONTROLLER
AREA | ZONE SERVICE | NUMBER OF SERVICE ZONES IN MECH ROOM | COMMON MECH. ROOM | ZONE DHWR SIZE(S) | ZONE DAILY WATER USAGE (LOAD) EA. ZONE | NUMBER OF BEDS IN ZONE | CONTROLLER TYPE | NUMBER OF ACTIVE CONTROLLERS | CONTROLLER MODEL No. | INDEPENDENT CELL ACTIVATION & MONITORING | REQUIRED TOTAL MAX. OUTPUT CAPACITY | REQUIRED INDEPENDENT OUTPUT RANGE FOR EA. CHAMBER CELL(S) | MULTI-USER PASSWORD PROTECTION | VARIABLE DC VOLTAGE OUTPUT CAPACITY | OPERATIONAL STATUS VOLT FREE CONTACT(S) | VISUAL ALARM | ETHERNET
DHWR | DOMESTIC HOT WATER (DHW) | 1 | N/A | ≤ 1.25" | ≤ 22,000 GPD | ≤ 150 | PLC with SOFTWARE AND INTERNAL MODULAR COMPONENTS | 1 | CSI-PHX-E1 (or) CSI-E1 | YES | 10A | 3A to 10A | YES | 0 - 180 VDC | 2 | YES - LED (GREEN / AMBER / RED) | YES
CSI CHAMBER CELL(S)
FLOW CELL MODEL NO. | LOCATION INSTALLED | INSTALLED & ACTIVE ION CHAMBER CELL(S) | BACKUP ION CHAMBER CELL(S) | EXTERNAL JACKET COMPOSITION | INTERNAL ELECTRODES INCLUDED IN EA. CELL | INSTALLATION ORIENTATION | SNAP IN ELECTRICAL CONNECTOR | 12H PRESSURE TOLERANCE | 12H TEMPERATURE TOLERANCE | PLUMBING CONNECTION | BI-DIRECTIONAL INTERNAL LAMINAR FLOW | REMARK NOTES
PHX-910 | DHWR | 1 | OPTIONAL | SCHEDULE 40 / 316 STAINLESS STEEL or ALUMINIUM | 8 | VERTICAL | YES | ≤ 250 PSI | ≤ 99 ℃ | GROOVED 3" IPS | YES | 1,2,3,4,5,6, 7,8,9,10,11
NOTES:
1 | CONTROLLER MUST INCLUDE INTEGRATED ELECTRICAL BREAKERS FOR EACH CHAMBER CELL(S) AND PLC
2 | IONIZATION SYSTEM TO PROVIDE AUTOMATED PLC VARIABLE VOLTAGE AND CONSTANT CURRENT
3 | CONTROLLER TO PROVIDE INDEPENDENT CHAMBER CELL ACTIVATION AND MONITORING
4 | PROVIDE 208VAC/P1/60Hz (15A) TO THE CSI CONTROLLER
5 | CONTROLLER MUST BE INSTALLED ≤ 8.00 FEET FROM CHAMBER CELL(S)
6 | CONTROLLER AND CHAMBER CELLS MUST BE INSTALLED AT NO LESS THAN 4.00 FEET FROM FLOOR
7 | CONTROLLER AND CHAMBER CELLS MUST BE INSTALLED AT NO MORE THAN 6.00 FEET FROM THE FLOOR
8 | CONTROLLER AND CHAMBER CELLS MUST BE EASILY ACCESSIBLE FOR MAINTENANCE
9 | PROVIDE ETHERNET CONNECTION FOR REMOTE ACCESS
10 | PROVIDE 2x BMS DRY CONTACT TO CONTROLLER (NC) : ONE FOR MAINTENANCE, ONE FOR FAULT
11 | PROVIDE ELECTRONIC FIELD COLORIMETER KIT (COPPER)